## Sheet1
Simulation Control |  | Small offices |  | Medium Offices |  | Large Offices
|  | Concrete | Curtain wall | Concrete | Curtain wall | Concrete | Curtain wall
Very Hot Humid (Honolulu, HI) | Heating energy [GJ] | 0 | 0 | 0.01 | 0.01 | 0 | 0
| Cooling energy [GJ] | 47.07 | 47.35 | 639.27 | 639.45 | 5905.35 | 5909.97
| Total Cosumption [GJ] | 162.47 | 162.75 | 1792.78 | 1793.02 | 30489.44 | 30496.67
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.256 | 0.257 | 3.468 | 3.468 | 5.232 | 5.232
| User Design Air Flow [m3/s] | 0.308 | 0.309 | 3.468 | 3.468 | 5.232 | 5.232
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00907 | 0.00907 | 0.00875 | 0.00875 | 0.00898 | 0.00898
| Outdoor Temperature at Peak Load [C] | 31.58 | 31.68 | 26.95 | 26.95 | 26.95 | 26.95
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.01437 | 0.01437 | 0.01436 | 0.01436 | 0.01436 | 0.01436
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.017 | 0.015 | 0.096 | 0.096
| User Design Air Flow [m3/s] | 0.065 | 0.065 | 0.425 | 0.425
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.08 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | 16.2 | 16.2 | 16.2 | 16.2
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.01152 | 0.01152 | 0.01152 | 0.01152
Hot Humid (Tampa, FL) | Heating energy [GJ] | 0.26 | 0.24 | 9.57 | 9.43 | 60.72 | 59.53
| Cooling energy [GJ] | 38.62 | 39.14 | 548.8 | 548.96 | 4653.55 | 4619.75
| Total Cosumption [GJ] | 154.77 | 155.23 | 1691.63 | 1691.77 | 28815.34 | 28805.69
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.264 | 0.263 | 3.483 | 3.483 | 5.268 | 5.268
| User Design Air Flow [m3/s] | 0.317 | 0.315 | 3.483 | 3.483 | 5.268 | 5.268
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.0906 | 0.00906 | 0.00875 | 0.00875 | 0.00898 | 0.00898
| Outdoor Temperature at Peak Load [C] | 33.22 | 33.22 | 28.05 | 28.05 | 28.05 | 28.05
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.01654 | 0.01654 | 0.01653 | 0.01653 | 0.01653 | 0.01653
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.045 | 0.044 | 0.233 | 0.233
| User Design Air Flow [m3/s] | 0.065 | 0.064 | 0.425 | 0.425
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | 4.6 | 4.6 | 4.6 | 4.6
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00526 | 0.00526 | 0.00526 | 0.00526
Hot Dry (Tucson, AZ) | Heating energy [GJ] | 0.36 | 0.32 | 14.11 | 14.01 | 80.02 | 79.04
| Cooling energy [GJ] | 33.68 | 34.12 | 434.17 | 434.34 | 4069.48 | 4072.28
| Total Cosumption [GJ] | 153.49 | 153.73 | 1589.39 | 1589.17 | 28954.24 | 28960.12
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.31 | 0.31 | 3.856 | 3.856 | 5.725 | 5.725
| User Design Air Flow [m3/s] | 0.372 | 0.372 | 3.856 | 3.856 | 5.725 | 5.725
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00902 | 0.00902 | 0.00875 | 0.00875 | 0.00875 | 0.00875
| Outdoor Temperature at Peak Load [C] | 39.47 | 39.47 | 30.96 | 30.96 | 30.96 | 30.96
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00563 | 0.00563 | 0.00562 | 0.00562 | 0.00562 | 0.00562
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.06 | 0.06 | 0.281 | 0.281
| User Design Air Flow [m3/s] | 0.072 | 0.072 | 0.425 | 0.425
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | 0.5 | 0.5 | 0.5 | 0.5
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00432 | 0.00432 | 0.00432 | 0.00432
Warm Dry (El Paso, TX) | Heating energy [GJ] | 2.52 | 2.23 | 49.97 | 49.47 | 344.56 | 340.31
| Cooling energy [GJ] | 22.95 | 23.47 | 308.51 | 308.77 | 3564.93 | 3577.4
| Total Cosumption [GJ] | 143.55 | 143.72 | 1576.33 | 1576.42 | 28547.31 | 28565.82
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.312 | 0.312 | 4.001 | 4.001 | 5.854 | 5.854
| User Design Air Flow [m3/s] | 0.374 | 0.374 | 4.001 | 4.001 | 5.854 | 5.854
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00904 | 0.00904 | 0.00875 | 0.00875 | 0.00875 | 0.00875
| Outdoor Temperature at Peak Load [C] | 37.15 | 37.15 | 28.48 | 28.48 | 28.48 | 28.48
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00687 | 0.00687 | 0.00687 | 0.00687 | 0.00687 | 0.00687
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.079 | 0.079 | 0.348 | 0.348
| User Design Air Flow [m3/s] | 0.095 | 0.095 | 0.425 | 0.425
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | -5.2 | -5.2 | -5.2 | -5.2
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00281 | 0.00281 | 0.00281 | 0.00281
Warm Marine (San Diego, CA) | Heating energy [GJ] | 0.34 | 0.28 | 9.79 | 9.7 | 44.25 | 43.51
| Cooling energy [GJ] | 13.82 | 14.8 | 193.56 | 194.16 | 2202.73 | 2210.14
| Total Cosumption [GJ] | 127.79 | 128.75 | 1398.75 | 1399.63 | 25911.68 | 25926.07
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.249 | 0.249 | 3.568 | 3.568 | 5.03 | 5.03
| User Design Air Flow [m3/s] | 0.299 | 0.299 | 3.568 | 3.568 | 5.03 | 5.03
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.0091 | 0.0091 | 0.00875 | 0.00875 | 0.00901 | 0.00901
| Outdoor Temperature at Peak Load [C] | 30.86 | 30.86 | 24.71 | 24.71 | 24.71 | 24.71
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00823 | 0.00823 | 0.00823 | 0.00823 | 0.00822 | 0.00822
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.049 | 0.049 | 0.249 | 0.249
| User Design Air Flow [m3/s] | 0.065 | 0.065 | 0.425 | 0.425
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | 3.8 | 3.8 | 3.8 | 3.8
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00506 | 0.00506 | 0.00506 | 0.00506
Mixed Dry (Albuquerque, NM) | Heating energy [GJ] | 4.97 | 4.69 | 88.62 | 87.5 | 764.49 | 755.42
| Cooling energy [GJ] | 16.8 | 17.46 | 224.77 | 225.28 | 2609.5 | 2623.67
| Total Cosumption [GJ] | 139.72 | 139.46 | 1538.72 | 1538.61 | 29155.42 | 29168.98
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.304 | 0.304 | 4.302 | 4.302 | 5.03 | 5.03
| User Design Air Flow [m3/s] | 0.365 | 0.365 | 4.302 | 4.302 | 5.03 | 5.03
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.009 | 0.009 | 0.00875 | 0.00875 | 0.00875 | 0.00875
| Outdoor Temperature at Peak Load [C] | 33.75 | 33.75 | 25.11 | 25.11 | 25.11 | 25.11
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.0057 | 0.0057 | 0.0057 | 0.0057 | 0.0057 | 0.0057
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.081 | 0.081 | 0.386 | 0.386
| User Design Air Flow [m3/s] | 0.097 | 0.097 | 0.425 | 0.425
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | -7.9 | -7.9 | -7.9 | -7.9
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00234 | 0.00234 | 0.00234 | 0.00234
Cold Humid (Rochester, MN) | Heating energy [GJ] | 65.03 | 60.25 | 611.34 | 606.61 | 2418.65 | 2373.38
| Cooling energy [GJ] | 8.79 | 9.4 | 157.16 | 157.44 | 2000.61 | 2014.95
| Total Cosumption [GJ] | 189.06 | 184.61 | 1980.59 | 1976.34 | 28801.73 | 28776.09
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.251 | 0.251 | 3.712 | 3.712 | 6.21 | 6.21
| User Design Air Flow [m3/s] | 0.301 | 0.301 | 3.712 | 3.712 | 6.21 | 6.21
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 24 | 24 | 24 | 24
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00911 | 0.00911 | 0.00875 | 0.00875 | 0.00875 | 0.00875
| Outdoor Temperature at Peak Load [C] | 30 | 30 | 23.36 | 23.36 | 23.36 | 23.36
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.01536 | 0.01536 | 0.1535 | 0.1535 | 0.1535 | 0.1535
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.11 | 0.11 | 0.476 | 0.476
| User Design Air Flow [m3/s] | 0.132 | 0.132 | 0.476 | 0.476
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21 | 21
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | -26.2 | -26.2 | -26.2 | -26.2
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00036 | 0.00036 | 0.00036 | 0.00036
Cold Dry (Great Falls, MO) | Heating energy [GJ] | 40.45 | 36.93 | 395.27 | 391.73 | 3202.36 | 3169.6
| Cooling energy [GJ] | 7.25 | 7.71 | 109.54 | 109.92 | 1449.07 | 1438.2
| Total Cosumption [GJ] | 164.09 | 160.97 | 1723.07 | 1720.26 | 30292.17 | 30254.11
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.274 | 0.274 | 4.047 | 4.047 | 5.782 | 5.782
| User Design Air Flow [m3/s] | 0.329 | 0.329 | 4.047 | 4.047 | 5.782 | 5.782
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00911 | 0.00911 | 0.00911 | 0.00911 | 0.00911 | 0.00911
| Outdoor Temperature at Peak Load [C] | 31.37 | 31.37 | 21.56 | 21.56 | 21.56 | 21.56
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.0063 | 0.0063 | 0.0063 | 0.0063 | 0.0063 | 0.0063
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.123 | 0.123 | 0.489 | 0.489
| User Design Air Flow [m3/s] | 0.148 | 0.148 | 0.489 | 0.489
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21.11 | 21.11
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21.11 | 21.11
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | -27.6 | -27.6 | -27.6 | -27.6
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00034 | 0.00034 | 0.00034 | 0.00034
Very Cold (International Falls, MN) | Heating energy [GJ] | 85.07 | 78.46 | 333.99 | 328.37 | 2372.54 | 2325.94
| Cooling energy [GJ] | 6.83 | 7.23 | 117.95 | 118.31 | 1637.35 | 1565.02
| Total Cosumption [GJ] | 206.76 | 200.45 | 1690.94 | 1685.91 | 28630.04 | 28643.46
Sensible Cooling
| Calculated Design Air Flow [m3/s] | 0.239 | 0.0243 | 3.695 | 3.694 | 5.295 | 5.295
| User Design Air Flow [m3/s] | 0.287 | 0.292 | 3.695 | 3.694 | 5.295 | 5.295
| Thermostat Setpoint Temperature at Peak Load [C] | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
| Indoor Temperature at Peak Load [C] | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00914 | 0.00914 | 0.00914 | 0.00914 | 0.00914 | 0.00914
| Outdoor Temperature at Peak Load [C] | 28.53 | 28.53 | 20.92 | 20.92 | 20.92 | 20.92
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.01272 | 0.01272 | 0.01272 | 0.01272 | 0.01272 | 0.01272
Sensible Heating
| Calculated Design Air Flow [m3/s] | 0.114 | 0.078 | 0.461 | 0.455
| User Design Air Flow [m3/s] | 0.137 | 0.094 | 0.461 | 0.455
| Thermostat Setpoint Temperature at Peak Load [C] | 21.11 | 21.11 | 21.11 | 21.11
| Indoor Temperature at Peak Load [C] | 21.11 | 21.11 | 21.11 | 21.11
| Indoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.008 | 0.008 | 0.008 | 0.008
| Outdoor Temperature at Peak Load [C] | -32.7 | -32.7 | -32.7 | -32.7
| Outdoor Humidity Ratio at Peak Load [kgWater/kgAir] | 0.00018 | 0.00018 | 0.00018 | 0.00018